## Blad1
Name | description | Modbus address (Base 0) | Register Type | Data Type (Big endian byte order) | Function code | Access | Units | Range | Basic control | Inputs | Outputs | Alarm
System Status | Modbus registers only accessable during System Status: Operation mode | 4x9001 | Holding | Uint 16 | FC 03 | R |  | [0 : Operation mode ¦ 2 : Configuration mode] | x
Outside air temperature |  | 3x0001 | Input | Float 32 | FC 04 | R | °C | -50 to 50 |  | X
Supply air temperature |  | 3x0005 | Input | Float 32 | FC 04 | R | °C | -50 to 80 |  | X
Extract air temperature |  | 3x0009 | Input | Float 32 | FC 04 | R | °C | -50 to 80 |  | X
Exhaust air temperature |  | 3x0013 | Input | Float 32 | FC 04 | R | °C | -50 to 80 |  | X
Room temperature | Temperature sensor on CI70 | 3x0017 | Input | Float 32 | FC 04 | R | °C | 0 to 50 |  | X
Supply air fan speed feedback |  | 3x0021 | Input | Float 32 | FC 04 | R | rpm | 0 to 18000 |  | X
Exhaust air fan speed feedback |  | 3x0025 | Input | Float 32 | FC 04 | R | rpm | 0 to 18000 |  | X
Frost protection temp.for heating coil | Only exists if Water heating is configured | 3x0033 | Input | Float 32 | FC 04 | R | Pa | -3000 to 3000 |  | X
Supply air pressure | Only exists if Fan control is configured as duct pressure (CI80) | 3x0037 | Input | Float 32 | FC 04 | R | Pa | -3000 to 3000 |  | X
Extract air pressure | Only exists if Fan control is configured as duct pressure (CI80) | 3x0041 | Input | Float 32 | FC 04 | R | Pa | -3000 to 3000 |  | X
Relative humidity for extract air | Only exists if configured on X3 | 3x0061 | Input | Float 32 | FC 04 | R | % | 0 to 100 |  | X
Room air quality input value (CU) | Only exists if configured on X3 | 3x0149 | Input | Float 32 | FC 04 | R | ppm | 0 to 2000 |  | X
Room air humidity 1 | RH value from CI77 - RH sensor 1. Only exists if CI75 - Wireless adapter is configured. | 3x1001 | Input | Float 32 | FC 04 | R | % | 0 to 100 |  | X
Room air humidity 2 | RH value from CI77 - RH sensor 2. Only exists if CI75 - Wireless adapter is configured. | 3x1003 | Input | Float 32 | FC 04 | R | % | 0 to 100 |  | X
Room air humidity 3 | RH value from CI77 - RH sensor 3. Only exists if CI75 - Wireless adapter is configured. | 3x1005 | Input | Float 32 | FC 04 | R | % | 0 to 100 |  | X
Room air quality 1 | CO2 value from CI76 - CO2 sensor. Only exists if CI75 - Wireless adapter is configured. | 3x1007 | Input | Float 32 | FC 04 | R | ppm | 0 to 2000 |  | X
High | Only exists if configured on DI1 or DI2 | 3x3006 | Input | Uint 16 | FC 04 | R |  | [0 : Inactive ¦ 1 : Active] |  | X
Home | Only exists if configured on DI1, DI2 or X8 | 3x3007 | Input | Uint 16 | FC 04 | R |  | [0 : Inactive ¦ 1 : Active] |  | X
Away | Only exists if configured on DI1, DI2 or X8 | 3x3008 | Input | Uint 16 | FC 04 | R |  | [0 : Inactive ¦ 1 : Active] |  | X
Stop | Only exists if configured on DI1 or DI2 | 3x3009 | Input | Uint 16 | FC 04 | R |  | [0 : Inactive ¦ 1 : Active] |  | X
Fireplace ventilation input | Only exists if configured on DI1 or DI2 | 3x3010 | Input | Uint 16 | FC 04 | R |  | [0 : Inactive ¦ 1 : Active] |  | X
Fume hood ventilation input | Cooker hood. Only exists if configured on DI1 or DI2 | 3x3011 | Input | Uint 16 | FC 04 | R |  | [0 : Inactive ¦ 1 : Active] |  | X
Fire damper feedback | Only exists if Fire damper is configured and fire damper feedback is selected on DI1, DI2 or X8 | 3x3013 | Input | Uint 16 | FC 04 | R |  | [0 : Inactive ¦ 1 : Active] |  | X
Emergency off | Only exists if configured on X8 | 3x3015 | Input | Uint 16 | FC 04 | R |  | [0 : Inactive ¦ 1 : Active] |  | X
CO detector | Only exists if configured on X8 | 3x3016 | Input | Uint 16 | FC 04 | R |  | [0 : Inactive ¦ 1 : Active] |  | X
Smoke/fire exhaust fan operation | Only exists if configured on X8 | 3x3017 | Input | Uint 16 | FC 04 | R |  | [0 : Inactive ¦ 1 : Active] |  | X
Smoke/fire supply fan operation | Only exists if configured on X8 | 3x3018 | Input | Uint 16 | FC 04 | R |  | [0 : Inactive ¦ 1 : Active] |  | X
Smoke/fire fan off operation | Only exists if configured on X8 | 3x3019 | Input | Uint 16 | FC 04 | R |  | [0 : Inactive ¦ 1 : Active] |  | X
Smoke/fire supply & exhaust fan op. | Only exists if configured on X8 | 3x3020 | Input | Uint 16 | FC 04 | R |  | [0 : Inactive ¦ 1 : Active] |  | X
Heating coil overtemperature detector | Only exists if Electric heater is configured | 3x3023 | Input | Uint 16 | FC 04 | R |  | [0 : Inactive ¦ 1 : Active] |  | X
Remaining time of rapid ventilation | Rapid ventilation = Ventilation mode Temporary High | 3x1035 | Input | Float 32 | FC 04 | R | min | 0 to 360 | X
Remaining time of fireplace ventilation |  | 3x1037 | Input | Float 32 | FC 04 | R | min | 0 to 360 | X
Setpoint temperature when home |  | 4x1155 | Holding | Float 32 | Read: FC 03 Write: FC 16 | RW | °C | 10 to 30 | X
Setpoint temperature when away |  | 4x1163 | Holding | Float 32 | Read: FC 03 Write: FC 16 | RW | °C | 10 to 30 | X
Heat recovery ventilation state | Present Ventilation mode | 3x3034 | Input | Uint 16 | FC 04 | R |  | [ 1 : Off ¦ 2 : Away ¦ 3 : Home ¦ 4 : High ¦ 5 : Fume hood ¦ 6 : Fireplace ¦ 7 : Temporary high] ¦ ] | X
Room operating mode | Select Ventilation mode. Only works if Comfort button [4x2040] = 1 If Comfort button [4x2040] = 0, this register is Away. (If ventilation mode control is active on a digital input, the digital input overrides this register.) | 4x2013 | Holding | Uint 16 | Read: FC 03 Write: FC 06 / 16 | RW |  | [ 1 : Stop ¦ 2 : Away ¦ 3 : Home ¦ 4 : High] ¦ ] | X
Comfort button | 0 = Ventilation mode Away after Away delay timer duration [4x1615]. Also overrides Room operating mode [4x2013]. 1 = Ventilation mode according to Room operating mode [4x2013]. | 4x2040 | Holding | Uint 16 | Read: FC 03 Write: FC 06 / 16 | RW |  | [0 : Inactive ¦ 1 : Active] | X
Trigger temporary rapid ventilation | Rapid ventilation = Ventilation mode Temporary High | 4x3006 | Holding | Uint 16 | Read: FC 03 Write: FC 06 / 16 | RW |  | [ 1 : Ready ¦ 2 : Trigger] ¦ ] | X
Trigger temporary fireplace ventilation |  | 4x3007 | Holding | Uint 16 | Read: FC 03 Write: FC 06 / 16 | RW |  | [ 1 : Ready ¦ 2 : Trigger] ¦ ] | X
Rapid ventilation runtime | Rapid ventilation = Ventilation mode Temporary High | 4x1103 | Holding | Uint 32 | Read: FC 03 Write: FC 16 | RW | min | 1 to 360 | X
Fireplace ventilation runtime |  | 4x1105 | Holding | Uint 32 | Read: FC 03 Write: FC 16 | RW | min | 0 to 360 | X
AWAY delay timer duration | Sets the delay time for Comfort button [4x2040] | 4x1615 | Holding | Uint 32 | Read: FC 03 Write: FC 16 | RW | min | 0 to 600 | X
Rotary heat exchanger speed |  | 4x0001 | Holding | Float 32 | Read: FC 03 Write: FC 16 | R | % | 0 to 100 |  |  | X
Supply air fan speed |  | 4x0005 | Holding | Float 32 | Read: FC 03 Write: FC 16 | R | % | 0 to 100 |  |  | X
Exhaust air fan speed |  | 4x0009 | Holding | Float 32 | Read: FC 03 Write: FC 16 | R | % | 0 to 100 |  |  | X
Heating coil electric position | Only exists if Electric heater is configured | 4x0013 | Holding | Float 32 | Read: FC 03 Write: FC 16 | R | % | 0 to 100 |  |  | X
Heating coil valve position | Only exists if Water heating is configured | 4x0017 | Holding | Float 32 | Read: FC 03 Write: FC 16 | R | % | 0 to 100 |  |  | X
Cooling coil valve position | Only exists if Water cooling is configured and Water cooling valve is selected on X7 | 4x0025 | Holding | Float 32 | Read: FC 03 Write: FC 16 | R | % | 0 to 100 |  |  | X
Heating coil pump command | Only exists if Water heating is configured | 4x2001 | Holding | Uint 16 | Read: FC 03 Write: FC 06 / 16 | R |  | [0 : Inactive ¦ 1 : Active] |  |  | X
Cooling coil pump command | Only exists if Water cooling or DX cooling is configured and Cooling pump is selected on Q1, Q2 or Q3 | 4x2004 | Holding | Uint 16 | Read: FC 03 Write: FC 06 / 16 | R |  | [0 : Inactive ¦ 1 : Active] |  |  | X
Outside air damper command | Only exists if Outside air damper is configured on Q1, Q2 or Q3 | 4x2007 | Holding | Uint 16 | Read: FC 03 Write: FC 06 / 16 | R |  | [0 : Inactive ¦ 1 : Active] |  |  | X
Fire damper command | Only exists if Fire damper is configured and fire damper command is selected on Q1, Q2 or Q3. | 4x2043 | Holding | Uint 16 | Read: FC 03 Write: FC 06 / 16 | R |  | [0 : Inactive ¦ 1 : Active] |  |  | X
A-Alarm code |  | 3x1021 | Input | Float 32 | FC 04 | R |  | 0 to 9999 |  |  |  | X
B-Alarm code |  | 3x1023 | Input | Float 32 | FC 04 | R |  | 0 to 9999 |  |  |  | X
Fault counter | Number of alarms in fault list | 3x1025 | Input | Float 32 | FC 04 | R |  | 0 to 2000 |  |  |  | X
Fault list number | Current place in fault list | 3x1027 | Input | Float 32 | FC 04 | R |  | 1 to 10000 |  |  |  | X
Display fault list | Alarm code for current place in fault list | 3x1029 | Input | Float 32 | FC 04 | R |  | 0 to 10000 |  |  |  | X
Operating time for filter replacement |  | 4x1269 | Holding | Float 32 | Read: FC 03 Write: FC 16 | RW | h | 0 to 99990 |  |  |  | X
Operating time filter |  | 4x1271 | Holding | Float 32 | Read: FC 03 Write: FC 16 | RW | h | 0 to 99999 |  |  |  | X
A-Alarm indication |  | 3x3001 | Input | Uint 16 | FC 04 | R |  | [ 1 : Normal ¦ 2 : Alarm] ¦ ] |  |  |  | X
A-Alarm state |  | 3x3002 | Input | Uint 16 | FC 04 | R |  | [ 1 : Acknowledged, unlocked ¦ 2 : Unacknowledged ¦ 3 : Locked] ¦ ] |  |  |  | X
B-Alarm indication |  | 3x3003 | Input | Uint 16 | FC 04 | R |  | [ 1 : Normal ¦ 2 : Alarm] ¦ ] |  |  |  | X
B-Alarm state |  | 3x3004 | Input | Uint 16 | FC 04 | R |  | [ 1 : Acknowledged, unlocked ¦ 2 : Unacknowledged ¦ 3 : Locked] ¦ ] |  |  |  | X
A-Alarm acknowledgement |  | 4x3002 | Holding | Uint 16 | Read: FC 03 Write: FC 06 / 16 | RW |  | [ 1 : Ready ¦ 2 : Acknowledge ¦ 3 : Reset] ¦ ] |  |  |  | X
B-Alarm acknowledgement |  | 4x3003 | Holding | Uint 16 | Read: FC 03 Write: FC 06 / 16 | RW |  | [ 1 : Ready ¦ 2 : Acknowledge] ¦ ] |  |  |  | X
Fault list operation | Operates the fault list. 3: Refresh, removes all inactive alarms. (All inactive alarms will also be removed if the product is powered down) | 4x3004 | Holding | Uint 16 | Read: FC 03 Write: FC 06 / 16 | RW |  | [ 1 : Ready ¦ 2 : Next fault ¦ 3 : Refresh] ¦ ] |  |  |  | X